## Current Capacity
Copper Wire TFE Insulated Current Carrying [A] |  |  |  | Conductor Current Capacity Matrix without Derating
|  |  |  | AWG | 1 | 00 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30
AWG | [A] |  |  | 1 | 1 | 169 | 147 | 108 | 81 | 60 | 44 | 33 | 25 | 19 | 13 | 9.2 | 6.5 | 4.5 | 3.3 | 2.5 | 1.8 | 1.3
00 | 169 |  |  | 00 | 1: 169; 00: 1
0 | 147 |  |  | 0 | 1: 147; 00: 1.1497; 0: 1
2 | 108 |  |  | 2 | 1: 108; 00: 1.5648; 0: 1.3611; 2: 1
4 | 81 |  |  | 4 | 1: 81; 00: 2.0864; 0: 1.8148; 2: 1.3333; 4: 1
6 | 60 |  |  | 6 | 1: 60; 00: 2.8167; 0: 2.45; 2: 1.8; 4: 1.35; 6: 1
8 | 44 |  |  | 8 | 1: 44; 00: 3.8409; 0: 3.3409; 2: 2.4545; 4: 1.8409; 6: 1.3636; 8: 1
10 | 33 |  |  | 10 | 1: 33; 00: 5.1212; 0: 4.4545; 2: 3.2727; 4: 2.4545; 6: 1.8182; 8: 1.3333; 10: 1
12 | 25 |  |  | 12 | 1: 25; 00: 6.76; 0: 5.88; 2: 4.32; 4: 3.24; 6: 2.4; 8: 1.76; 10: 1.32; 12: 1
14 | 19 |  |  | 14 | 1: 19; 00: 8.8947; 0: 7.7368; 2: 5.6842; 4: 4.2632; 6: 3.1579; 8: 2.3158; 10: 1.7368; 12: 1.3158; 14: 1
16 | 13 |  |  | 16 | 13 | 13 | 11.3077 | 8.3077 | 6.2308 | 4.6154 | 3.3846 | 2.5385 | 1.9231 | 1.4615 | 1
18 | 9.2 |  |  | 18 | 9.2 | 18.3696 | 15.9783 | 11.7391 | 8.8043 | 6.5217 | 4.7826 | 3.587 | 2.7174 | 2.0652 | 1.413 | 1
20 | 6.5 |  |  | 20 | 6.5 | 26 | 22.6154 | 16.6154 | 12.4615 | 9.2308 | 6.7692 | 5.0769 | 3.8462 | 2.9231 | 2 | 1.4154 | 1
22 | 4.5 |  |  | 22 | 4.5 | 37.5556 | 32.6667 | 24 | 18 | 13.3333 | 9.7778 | 7.3333 | 5.5556 | 4.2222 | 2.8889 | 2.0444 | 1.4444 | 1
24 | 3.3 |  |  | 24 | 3.3 | 51.2121 | 44.5455 | 32.7273 | 24.5455 | 18.1818 | 13.3333 | 10 | 7.5758 | 5.7576 | 3.9394 | 2.7879 | 1.9697 | 1.3636 | 1
26 | 2.5 |  |  | 26 | 2.5 | 67.6 | 58.8 | 43.2 | 32.4 | 24 | 17.6 | 13.2 | 10 | 7.6 | 5.2 | 3.68 | 2.6 | 1.8 | 1.32 | 1
28 | 1.8 |  |  | 28 | 1.8 | 93.8889 | 81.6667 | 60 | 45 | 33.3333 | 24.4444 | 18.3333 | 13.8889 | 10.5556 | 7.2222 | 5.1111 | 3.6111 | 2.5 | 1.8333 | 1.3889 | 1
30 | 1.3 |  |  | 30 | 1.3 | 130 | 113.0769 | 83.0769 | 62.3077 | 46.1538 | 33.8462 | 25.3846 | 19.2308 | 14.6154 | 10 | 7.0769 | 5 | 3.4615 | 2.5385 | 1.9231 | 1.3846 | 1
AS50881D Current Carrying [A] |  |  |  | Conductor Current Capacity Matrix without Derating
105 °C | Wire Temperature Rating °C |  |  | AWG | 1 | 0000 | 000 | 00 | 0 | 1 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26
AWG | 105 °C | 150 °C | 200 °C | 1 | 1 | 204 | 172 | 147 | 128 | 113 | 95 | 68 | 50 | 38 | 17 | 13 | 10 | 7 | 6 | 4 | 3 | 3 | 2
0000 | 204 | 310 | 395 | 0000 | 1: 204; 00: 1
000 | 172 | 262 | 335 | 000 | 1: 172; 00: 1.186; 0: 1
00 | 147 | 222 | 285 | 00 | 1: 147; 00: 1.3878; 0: 1.1701; 2: 1
0 | 128 | 192 | 243 | 0 | 1: 128; 00: 1.5938; 0: 1.3438; 2: 1.1484; 4: 1
1 | 113 | 166 | 210 | 1 | 1: 113; 00: 1.8053; 0: 1.5221; 2: 1.3009; 4: 1.1327; 6: 1
2 | 95 | 141 | 179 | 2 | 1: 95; 00: 2.1474; 0: 1.8105; 2: 1.5474; 4: 1.3474; 6: 1.1895; 8: 1
4 | 68 | 103 | 133 | 4 | 1: 68; 00: 3; 0: 2.5294; 2: 2.1618; 4: 1.8824; 6: 1.6618; 8: 1.3971; 10: 1
6 | 50 | 76 | 97 | 6 | 1: 50; 00: 4.08; 0: 3.44; 2: 2.94; 4: 2.56; 6: 2.26; 8: 1.9; 10: 1.36; 12: 1
8 | 38 | 57 | 71 | 8 | 1: 38; 00: 5.3684; 0: 4.5263; 2: 3.8684; 4: 3.3684; 6: 2.9737; 8: 2.5; 10: 1.7895; 12: 1.3158; 14: 1
10 | 17 | 26 | 32 | 10 | 17 | 12 | 10.1176 | 8.6471 | 7.5294 | 6.6471 | 5.5882 | 4 | 2.9412 | 2.2353 | 1
12 | 13 | 19 | 25 | 12 | 13 | 15.6923 | 13.2308 | 11.3077 | 9.8462 | 8.6923 | 7.3077 | 5.2308 | 3.8462 | 2.9231 | 1.3077 | 1
14 | 10 | 14 | 18 | 14 | 10 | 20.4 | 17.2 | 14.7 | 12.8 | 11.3 | 9.5 | 6.8 | 5 | 3.8 | 1.7 | 1.3 | 1
16 | 7 | 11 | 14 | 16 | 7 | 29.1429 | 24.5714 | 21 | 18.2857 | 16.1429 | 13.5714 | 9.7143 | 7.1429 | 5.4286 | 2.4286 | 1.8571 | 1.4286 | 1
18 | 6 | 9 | 12 | 18 | 6 | 34 | 28.6667 | 24.5 | 21.3333 | 18.8333 | 15.8333 | 11.3333 | 8.3333 | 6.3333 | 2.8333 | 2.1667 | 1.6667 | 1.1667 | 1
20 | 4 | 7 | 9 | 20 | 4 | 51 | 43 | 36.75 | 32 | 28.25 | 23.75 | 17 | 12.5 | 9.5 | 4.25 | 3.25 | 2.5 | 1.75 | 1.5 | 1
22 | 3 | 5 | 6 | 22 | 3 | 68 | 57.3333 | 49 | 42.6667 | 37.6667 | 31.6667 | 22.6667 | 16.6667 | 12.6667 | 5.6667 | 4.3333 | 3.3333 | 2.3333 | 2 | 1.3333 | 1 | 1
24 | 3 | 4 | 5 | 24 | 3 | 68 | 57.3333 | 49 | 42.6667 | 37.6667 | 31.6667 | 22.6667 | 16.6667 | 12.6667 | 5.6667 | 4.3333 | 3.3333 | 2.3333 | 2 | 1.3333 | 1 | 1
26 | 2 | 3 | 4 | 26 | 2 | 102 | 86 | 73.5 | 64 | 56.5 | 47.5 | 34 | 25 | 19 | 8.5 | 6.5 | 5 | 3.5 | 3 | 2 | 1.5 | 1.5 | 1

## Conductor Area
Conductor Area Matrix [Col/Row] Ratio
|  |  | AWG | 1 | 0000 | 000 | 00 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
AWG | Dia [mm] | Area [mm²] | 1 | 1 | 107.2193 | 85.0304 | 67.4289 | 53.473 | 42.4061 | 33.6297 | 26.6692 | 21.1499 | 16.7726 | 13.3013 | 10.5485 | 8.3653 | 6.6339 | 5.2608 | 4.1721 | 3.3087 | 2.6239 | 2.0808 | 1.6502 | 1.3086 | 1.0378 | 0.82307 | 0.65268 | 0.51759 | 0.41044 | 0.32553 | 0.25814 | 0.20476 | 0.16238 | 0.12876 | 0.10213 | 0.080979 | 0.064198 | 0.05091 | 0.040399 | 0.032016 | 0.02539 | 0.020131 | 0.015971 | 0.012668 | 0.010047 | 0.0079643 | 0.0063194 | 0.005014
0000 | 11.684 | 107.2193 | 0000 | 1: 107.2193; 0000: 1
000 | 10.405 | 85.0304 | 000 | 1: 85.0304; 0000: 1.261; 000: 1
00 | 9.2657 | 67.4289 | 00 | 1: 67.4289; 0000: 1.5901; 000: 1.261; 00: 1
0 | 8.2513 | 53.473 | 0 | 1: 53.473; 0000: 2.0051; 000: 1.5902; 00: 1.261; 0: 1
1 | 7.348 | 42.4061 | 1 | 1: 42.4061; 0000: 2.5284; 000: 2.0051; 00: 1.5901; 0: 1.261; 1: 1
2 | 6.5436 | 33.6297 | 2 | 1: 33.6297; 0000: 3.1882; 000: 2.5284; 00: 2.005; 0: 1.5901; 1: 1.261; 2: 1
3 | 5.8272 | 26.6692 | 3 | 1: 26.6692; 0000: 4.0203; 000: 3.1883; 00: 2.5283; 0: 2.005; 1: 1.5901; 2: 1.261; 3: 1
4 | 5.1893 | 21.1499 | 4 | 1: 21.1499; 0000: 5.0695; 000: 4.0204; 00: 3.1882; 0: 2.5283; 1: 2.005; 2: 1.5901; 3: 1.261; 4: 1
5 | 4.6212 | 16.7726 | 5 | 1: 16.7726; 0000: 6.3925; 000: 5.0696; 00: 4.0202; 0: 3.1881; 1: 2.5283; 2: 2.005; 3: 1.59; 4: 1.261; 5: 1
6 | 4.1153 | 13.3013 | 6 | 1: 13.3013; 0000: 8.0608; 000: 6.3927; 00: 5.0694; 0: 4.0201; 1: 3.1881; 2: 2.5283; 3: 2.005; 4: 1.5901; 5: 1.261; 6: 1
7 | 3.6648 | 10.5485 | 7 | 1: 10.5485; 0000: 10.1644; 000: 8.0609; 00: 6.3923; 0: 5.0693; 1: 4.0201; 2: 3.1881; 3: 2.5282; 4: 2.005; 5: 1.59; 6: 1.261; 7: 1
8 | 3.2636 | 8.3653 | 8 | 1: 8.3653; 0000: 12.8171; 000: 10.1646; 00: 8.0605; 0: 6.3922; 1: 5.0693; 2: 4.0201; 3: 3.1881; 4: 2.5283; 5: 2.005; 6: 1.59; 7: 1.261; 8: 1
9 | 2.9063 | 6.6339 | 9 | 1: 6.6339; 0000: 16.1623; 000: 12.8175; 00: 10.1643; 0: 8.0605; 1: 6.3923; 2: 5.0694; 3: 4.0201; 4: 3.1881; 5: 2.5283; 6: 2.005; 7: 1.5901; 8: 1.261; 9: 1
10 | 2.5881 | 5.2608 | 10 | 1: 5.2608; 0000: 20.3808; 000: 16.163; 00: 12.8172; 0: 10.1644; 1: 8.0608; 2: 6.3925; 3: 5.0694; 4: 4.0203; 5: 3.1882; 6: 2.5284; 7: 2.0051; 8: 1.5901; 9: 1.261; 10: 1
11 | 2.3048 | 4.1721 | 11 | 1: 4.1721; 0000: 25.699; 000: 20.3806; 00: 16.1618; 0: 12.8168; 1: 10.1642; 2: 8.0606; 3: 6.3922; 4: 5.0693; 5: 4.0202; 6: 3.1881; 7: 2.5283; 8: 2.0051; 9: 1.5901; 10: 1.2609; 11: 1
12 | 2.0525 | 3.3087 | 12 | 1: 3.3087; 0000: 32.4054; 000: 25.6991; 00: 20.3793; 0: 16.1614; 1: 12.8166; 2: 10.1641; 3: 8.0603; 4: 6.3922; 5: 5.0692; 6: 4.0201; 7: 3.1881; 8: 2.5283; 9: 2.005; 10: 1.59; 11: 1.261; 12: 1
13 | 1.8278 | 2.6239 | 13 | 1: 2.6239; 0000: 40.8626; 000: 32.4061; 00: 25.698; 0: 20.3792; 1: 16.1615; 2: 12.8167; 3: 10.1639; 4: 8.0605; 5: 6.3922; 6: 5.0693; 7: 4.0202; 8: 3.1881; 9: 2.5283; 10: 2.005; 11: 1.59; 12: 1.261; 13: 1
14 | 1.6277 | 2.0808 | 14 | 1: 2.0808; 0000: 51.5269; 000: 40.8635; 00: 32.4047; 0: 25.6978; 1: 20.3793; 2: 16.1616; 3: 12.8165; 4: 10.1641; 5: 8.0605; 6: 6.3923; 7: 5.0693; 8: 4.0202; 9: 3.1881; 10: 2.5282; 11: 2.005; 12: 1.5901; 13: 1.261; 14: 1
15 | 1.4495 | 1.6502 | 15 | 1: 1.6502; 0000: 64.9751; 000: 51.5285; 00: 40.862; 0: 32.4047; 1: 25.6981; 2: 20.3797; 3: 16.1616; 4: 12.8168; 5: 10.1642; 6: 8.0606; 7: 6.3924; 8: 5.0694; 9: 4.0202; 10: 3.1881; 11: 2.5283; 12: 2.0051; 13: 1.5901; 14: 1.261; 15: 1
16 | 1.2908 | 1.3086 | 16 | 1: 1.3086; 0000: 81.9342; 000: 64.978; 00: 51.5274; 0: 40.8627; 1: 32.4056; 2: 25.699; 3: 20.3799; 4: 16.1622; 5: 12.8172; 6: 10.1645; 7: 8.0609; 8: 6.3926; 9: 5.0695; 10: 4.0202; 11: 3.1882; 12: 2.5284; 13: 2.0051; 14: 1.5901; 15: 1.261; 16: 1
17 | 1.1495 | 1.0378 | 17 | 1: 1.0378; 0000: 103.3154; 000: 81.9344; 00: 64.9738; 0: 51.526; 1: 40.8621; 2: 32.4053; 3: 25.6982; 4: 20.3798; 5: 16.1619; 6: 12.817; 7: 10.1644; 8: 8.0608; 9: 6.3924; 10: 5.0693; 11: 4.0202; 12: 3.1882; 13: 2.5284; 14: 2.0051; 15: 1.5901; 16: 1.261; 17: 1
18 | 1.0237 | 0.82307 | 18 | 1: 0.82307; 0000: 130.268; 000: 103.3091; 00: 81.924; 0: 64.968; 1: 51.522; 2: 40.859; 3: 32.4022; 4: 25.6964; 5: 20.3781; 6: 16.1606; 7: 12.8161; 8: 10.1636; 9: 8.06; 10: 6.3917; 11: 5.069; 12: 4.02; 13: 3.188; 14: 2.5282; 15: 2.0049; 16: 1.5899; 17: 1.2609; 18: 1
19 | 0.9116 | 0.65268 | 19 | 1: 0.65268; 0000: 164.2761; 000: 130.2793; 00: 103.3113; 0: 81.9287; 1: 64.9725; 2: 51.5258; 3: 40.8612; 4: 32.4048; 5: 25.6981; 6: 20.3795; 7: 16.1619; 8: 12.817; 9: 10.1642; 10: 8.0603; 11: 6.3923; 12: 5.0694; 13: 4.0202; 14: 3.1882; 15: 2.5283; 16: 2.005; 17: 1.59; 18: 1.2611; 19: 1
20 | 0.8118 | 0.51759 | 20 | 1: 0.51759; 0000: 207.15; 000: 164.2805; 00: 130.2742; 0: 103.311; 1: 81.9295; 2: 64.9734; 3: 51.5254; 4: 40.862; 5: 32.405; 6: 25.6983; 7: 20.3799; 8: 16.162; 9: 12.8169; 10: 10.164; 11: 8.0606; 12: 6.3925; 13: 5.0694; 14: 4.0202; 15: 3.1881; 16: 2.5282; 17: 2.005; 18: 1.5902; 19: 1.261; 20: 1
21 | 0.7229 | 0.41044 | 21 | 1: 0.41044; 0000: 261.2322; 000: 207.1704; 00: 164.2858; 0: 130.2832; 1: 103.3194; 2: 81.9364; 3: 64.9776; 4: 51.5301; 5: 40.8651; 6: 32.4076; 7: 25.7007; 8: 20.3816; 9: 16.1631; 10: 12.8176; 11: 10.1651; 12: 8.0614; 13: 6.3929; 14: 5.0698; 15: 4.0205; 16: 3.1883; 17: 2.5285; 18: 2.0053; 19: 1.5902; 20: 1.2611; 21: 1
22 | 0.6438 | 0.32553 | 22 | 0.32553 | 329.3678 | 261.2054 | 207.1355 | 164.2642 | 130.2676 | 103.3074 | 81.9253 | 64.9704 | 51.5238 | 40.8603 | 32.404 | 25.6976 | 20.3788 | 16.1607 | 12.8164 | 10.164 | 8.0604 | 6.3921 | 5.0691 | 4.0199 | 3.188 | 2.5284 | 2.005 | 1.59 | 1.2608 | 1
23 | 0.5733 | 0.25814 | 23 | 0.25814 | 415.3548 | 329.3975 | 261.2117 | 207.1481 | 164.2761 | 130.2776 | 103.3132 | 81.932 | 64.9749 | 51.5275 | 40.8636 | 32.4063 | 25.699 | 20.3797 | 16.1623 | 12.8175 | 10.1647 | 8.0609 | 6.3925 | 5.0694 | 4.0203 | 3.1885 | 2.5284 | 2.0051 | 1.59 | 1.2611 | 1
24 | 0.5106 | 0.20476 | 24 | 0.20476 | 523.6263 | 415.2623 | 329.3024 | 261.1459 | 207.0984 | 164.2373 | 130.2442 | 103.2894 | 81.9121 | 64.9593 | 51.5156 | 40.8538 | 32.3981 | 25.6922 | 20.3753 | 16.1586 | 12.8143 | 10.1622 | 8.0589 | 6.3908 | 5.0682 | 4.0196 | 3.1875 | 2.5278 | 2.0044 | 1.5898 | 1.2607 | 1
25 | 0.4547 | 0.16238 | 25 | 0.16238 | 660.2877 | 523.6417 | 415.2471 | 329.3024 | 261.149 | 207.1017 | 164.2366 | 130.247 | 103.2903 | 81.913 | 64.9607 | 51.5162 | 40.8537 | 32.3976 | 25.6931 | 20.3759 | 16.1587 | 12.8144 | 10.1622 | 8.0588 | 6.391 | 5.0687 | 4.0194 | 3.1875 | 2.5276 | 2.0047 | 1.5897 | 1.261 | 1
26 | 0.4049 | 0.12876 | 26 | 0.12876 | 832.698 | 660.3719 | 523.6739 | 415.2878 | 329.3387 | 261.1788 | 207.1211 | 164.2563 | 130.2609 | 103.3017 | 81.9228 | 64.9678 | 51.5211 | 40.857 | 32.4019 | 25.6963 | 20.378 | 16.1604 | 12.8157 | 10.163 | 8.0598 | 6.3922 | 5.0689 | 4.0198 | 3.1876 | 2.5282 | 2.0048 | 1.5903 | 1.2611 | 1
27 | 0.3606 | 0.10213 | 27 | 0.10213 | 1049.8606 | 832.5929 | 660.2449 | 523.5924 | 415.2282 | 329.2927 | 261.137 | 207.0933 | 164.2321 | 130.2421 | 103.2878 | 81.911 | 64.9575 | 51.5123 | 40.8522 | 32.3978 | 25.6925 | 20.375 | 16.1579 | 12.8135 | 10.1617 | 8.0592 | 6.3908 | 5.0681 | 4.0189 | 3.1875 | 2.5276 | 2.005 | 1.59 | 1.2608 | 1
28 | 0.3211 | 0.080979 | 28 | 0.080979 | 1324.0442 | 1050.0345 | 832.6756 | 660.3347 | 523.67 | 415.2913 | 329.336 | 261.1782 | 207.1233 | 164.2564 | 130.2627 | 103.3031 | 81.9219 | 64.9653 | 51.5212 | 40.8588 | 32.4024 | 25.6962 | 20.3777 | 16.1598 | 12.8156 | 10.164 | 8.0599 | 6.3917 | 5.0685 | 4.02 | 3.1877 | 2.5286 | 2.0053 | 1.5901 | 1.2612 | 1
29 | 0.2859 | 0.064198 | 29 | 0.064198 | 1670.1473 | 1324.5119 | 1050.3358 | 832.9452 | 660.5565 | 523.8479 | 415.424 | 329.4498 | 261.265 | 207.1928 | 164.3131 | 130.3063 | 103.3362 | 81.9471 | 64.9887 | 51.5392 | 40.8723 | 32.4131 | 25.7044 | 20.384 | 16.1655 | 12.8209 | 10.1667 | 8.0625 | 6.3933 | 5.0708 | 4.021 | 3.1896 | 2.5294 | 2.0057 | 1.5908 | 1.2614 | 1
30 | 0.2546 | 0.05091 | 30 | 0.05091 | 2106.0385 | 1670.1957 | 1324.4625 | 1050.3353 | 832.9549 | 660.5667 | 523.8453 | 415.4328 | 329.4524 | 261.268 | 207.1971 | 164.3149 | 130.3059 | 103.3345 | 81.9501 | 64.9904 | 51.5395 | 40.8726 | 32.413 | 25.704 | 20.3846 | 16.167 | 12.8201 | 10.1667 | 8.0619 | 6.3942 | 5.0705 | 4.022 | 3.1896 | 2.5292 | 2.006 | 1.5906 | 1.261 | 1
31 | 0.2268 | 0.040399 | 31 | 0.040399 | 2653.976 | 2104.7381 | 1669.0539 | 1323.6058 | 1049.6686 | 832.4294 | 660.1365 | 523.5178 | 415.1676 | 329.2433 | 261.1046 | 207.0655 | 164.2082 | 130.2195 | 103.2715 | 81.8993 | 64.9488 | 51.5066 | 40.8461 | 32.3916 | 25.6881 | 20.3732 | 16.1556 | 12.8119 | 10.1595 | 8.0578 | 6.3897 | 5.0685 | 4.0194 | 3.1872 | 2.5279 | 2.0044 | 1.5891 | 1.2602 | 1
32 | 0.2019 | 0.032016 | 32 | 0.032016 | 3348.9638 | 2655.8989 | 2106.1235 | 1670.214 | 1324.5418 | 1050.4148 | 833.0042 | 660.6097 | 523.8861 | 415.4611 | 329.4791 | 261.2891 | 207.2088 | 164.3196 | 130.3148 | 103.346 | 81.9567 | 64.9944 | 51.5423 | 40.8738 | 32.4149 | 25.7083 | 20.3862 | 16.1669 | 12.8199 | 10.1679 | 8.0629 | 6.3957 | 5.072 | 4.0218 | 3.1899 | 2.5293 | 2.0052 | 1.5902 | 1.2619 | 1
33 | 0.1798 | 0.02539 | 33 | 0.02539 | 4222.8312 | 3348.9202 | 2655.6883 | 2106.034 | 1670.1632 | 1324.5066 | 1050.3656 | 832.9869 | 660.5872 | 523.8701 | 415.4523 | 329.4689 | 261.2772 | 207.1967 | 164.3187 | 130.3128 | 103.3423 | 81.9538 | 64.9916 | 51.5393 | 40.8732 | 32.4165 | 25.7057 | 20.3854 | 16.1651 | 12.821 | 10.1668 | 8.0646 | 6.3954 | 5.0713 | 4.0223 | 3.1893 | 2.5284 | 2.0051 | 1.5911 | 1.2609 | 1
34 | 0.1601 | 0.020131 | 34 | 0.020131 | 5325.9911 | 4223.7821 | 3349.4524 | 2656.2081 | 2106.4717 | 1670.5167 | 1324.7599 | 1050.5939 | 833.157 | 660.7244 | 523.9838 | 415.5384 | 329.5325 | 261.3241 | 207.2449 | 164.3553 | 130.3391 | 103.3632 | 81.9698 | 65.0033 | 51.5508 | 40.8849 | 32.421 | 25.7108 | 20.388 | 16.1703 | 12.8228 | 10.1714 | 8.0662 | 6.3961 | 5.073 | 4.0225 | 3.1889 | 2.5289 | 2.0068 | 1.5903 | 1.2612 | 1
35 | 0.1426 | 0.015971 | 35 | 0.015971 | 6713.4235 | 5324.0867 | 4221.9921 | 3348.1561 | 2655.2123 | 2105.69 | 1669.8628 | 1324.276 | 1050.1963 | 832.8446 | 660.4828 | 523.7871 | 415.3764 | 329.3996 | 261.2326 | 207.1702 | 164.2927 | 130.2896 | 103.3231 | 81.9368 | 64.9799 | 51.5355 | 40.8667 | 32.4085 | 25.6991 | 20.3828 | 16.1631 | 12.821 | 10.1674 | 8.0623 | 6.3946 | 5.0704 | 4.0197 | 3.1877 | 2.5296 | 2.0046 | 1.5898 | 1.2605 | 1
36 | 0.127 | 0.012668 | 36 | 0.012668 | 8464 | 6712.383 | 5322.9088 | 4221.2134 | 3347.5791 | 2654.7648 | 2105.2923 | 1669.5911 | 1324.043 | 1050.0151 | 832.7087 | 660.3686 | 523.689 | 415.2931 | 329.351 | 261.1914 | 207.1333 | 164.2636 | 130.2654 | 103.3024 | 81.9239 | 64.9738 | 51.523 | 40.8593 | 32.4003 | 25.6977 | 20.3778 | 16.1642 | 12.8187 | 10.1645 | 8.062 | 6.3925 | 5.0678 | 4.0189 | 3.1892 | 2.5273 | 2.0043 | 1.5892 | 1.2608 | 1
37 | 0.1131 | 0.010047 | 37 | 0.010047 | 10672.2966 | 8463.6746 | 6711.6803 | 5322.5475 | 4220.978 | 3347.4051 | 2654.5728 | 2105.1951 | 1669.4919 | 1323.9689 | 1049.9663 | 832.6618 | 660.3219 | 523.6449 | 415.2803 | 329.3375 | 261.1753 | 207.1207 | 164.2522 | 130.2545 | 103.2982 | 81.9257 | 64.9656 | 51.5196 | 40.8537 | 32.4024 | 25.6944 | 20.3815 | 16.1631 | 12.8165 | 10.1654 | 8.0604 | 6.39 | 5.0675 | 4.0212 | 3.1867 | 2.5273 | 2.0038 | 1.5897 | 1.2609 | 1
38 | 0.1007 | 0.0079643 | 38 | 0.0079643 | 13462.4516 | 10676.4096 | 8466.3755 | 6714.0692 | 5324.5064 | 4222.5475 | 3348.5818 | 2655.5753 | 2105.9623 | 1670.1061 | 1324.4684 | 1050.3521 | 832.9558 | 660.5461 | 523.8507 | 415.4391 | 329.4567 | 261.2701 | 207.1942 | 164.3081 | 130.3044 | 103.3443 | 81.9501 | 64.9889 | 51.5344 | 40.8736 | 32.4119 | 25.71 | 20.3888 | 16.1673 | 12.8231 | 10.1677 | 8.0606 | 6.3923 | 5.0726 | 4.0199 | 3.188 | 2.5277 | 2.0053 | 1.5906 | 1.2614 | 1
39 | 0.0897 | 0.0063194 | 39 | 0.0063194 | 16966.7324 | 13455.4827 | 10670.176 | 8461.7437 | 6710.4773 | 5321.6781 | 4220.2187 | 3346.8224 | 2654.145 | 2104.8353 | 1669.228 | 1323.7591 | 1049.7744 | 832.4865 | 660.2092 | 523.5781 | 415.2145 | 329.2789 | 261.1269 | 207.0776 | 164.2227 | 130.2448 | 103.2818 | 81.9055 | 64.9489 | 51.513 | 40.8488 | 32.4024 | 25.696 | 20.3756 | 16.1609 | 12.8143 | 10.1588 | 8.0562 | 6.3929 | 5.0663 | 4.0179 | 3.1856 | 2.5273 | 2.0046 | 1.5898 | 1.2603 | 1
40 | 0.0799 | 0.005014 | 40 | 0.005014 | 21384.0292 | 16958.624 | 13448.1613 | 10664.7627 | 8457.5532 | 6707.1795 | 5318.9547 | 4218.1692 | 3345.1529 | 2652.8301 | 2103.8123 | 1668.4004 | 1323.0837 | 1049.2248 | 832.095 | 659.8919 | 523.3157 | 415.0068 | 329.1114 | 260.9903 | 206.9781 | 164.1541 | 130.1712 | 103.2297 | 81.8583 | 64.9245 | 51.4838 | 40.8383 | 32.3859 | 25.6804 | 20.3684 | 16.1505 | 12.8037 | 10.1537 | 8.0574 | 6.3853 | 5.0639 | 4.015 | 3.1853 | 2.5265 | 2.0037 | 1.5884 | 1.2604 | 1

## Model
AWG | Dia-mils | TPI | Dia-mm | Area-mm^2 | Circ-mils | Ohms/Kft | Ft/Ohm | Ft/Lb | Ohms/Lb | Lb/Kft | *Amps | MaxAmps
0000 | 459.99 | 2.174 | 11.684 | 107.2193 | 211592 | 0.049 | 20402 | 1.5613 | 0.0001 | 640.48 | 282.12 | 423.18
000 | 409.63 | 2.4412 | 10.405 | 85.0304 | 167800 | 0.0618 | 16180 | 1.9688 | 0.0001 | 507.93 | 223.73 | 335.6
00 | 364.79 | 2.7413 | 9.2657 | 67.4289 | 133072 | 0.0779 | 12831 | 2.4826 | 0.0002 | 402.8 | 177.43 | 266.14
0 | 324.85 | 3.0783 | 8.2513 | 53.473 | 105531 | 0.0983 | 10175 | 3.1305 | 0.0003 | 319.44 | 140.71 | 211.06
1 | 289.29 | 3.4567 | 7.348 | 42.4061 | 83690 | 0.1239 | 8069.5 | 3.9475 | 0.0005 | 253.33 | 111.59 | 167.38
2 | 257.62 | 3.8817 | 6.5436 | 33.6297 | 66369 | 0.1563 | 6399.4 | 4.9777 | 0.0008 | 200.9 | 88.492 | 132.74
3 | 229.42 | 4.3588 | 5.8272 | 26.6692 | 52633 | 0.197 | 5075 | 6.2767 | 0.0012 | 159.32 | 70.177 | 105.27
4 | 204.3 | 4.8947 | 5.1893 | 21.1499 | 41740 | 0.2485 | 4024.7 | 7.9148 | 0.002 | 126.35 | 55.653 | 83.48
5 | 181.94 | 5.4964 | 4.6212 | 16.7726 | 33101 | 0.3133 | 3191.7 | 9.9804 | 0.0031 | 100.2 | 44.135 | 66.203
6 | 162.02 | 6.1721 | 4.1153 | 13.3013 | 26251 | 0.3951 | 2531.1 | 12.585 | 0.005 | 79.46 | 35.001 | 52.501
7 | 144.28 | 6.9308 | 3.6648 | 10.5485 | 20818 | 0.4982 | 2007.3 | 15.869 | 0.0079 | 63.014 | 27.757 | 41.635
8 | 128.49 | 7.7828 | 3.2636 | 8.3653 | 16509 | 0.6282 | 1591.8 | 20.011 | 0.0126 | 49.973 | 22.012 | 33.018
9 | 114.42 | 8.7396 | 2.9063 | 6.6339 | 13092 | 0.7921 | 1262.4 | 25.233 | 0.02 | 39.63 | 17.456 | 26.185
10 | 101.9 | 9.814 | 2.5881 | 5.2608 | 10383 | 0.9989 | 1001.1 | 31.819 | 0.0318 | 31.428 | 13.844 | 20.765
11 | 90.741 | 11.02 | 2.3048 | 4.1721 | 8233.9 | 1.2596 | 793.93 | 40.122 | 0.0505 | 24.924 | 10.978 | 16.468
12 | 80.807 | 12.375 | 2.0525 | 3.3087 | 6529.8 | 1.5883 | 629.61 | 50.593 | 0.0804 | 19.765 | 8.7064 | 13.06
13 | 71.961 | 13.896 | 1.8278 | 2.6239 | 5178.3 | 2.0028 | 499.31 | 63.797 | 0.1278 | 15.675 | 6.9045 | 10.357
14 | 64.083 | 15.605 | 1.6277 | 2.0808 | 4106.6 | 2.5255 | 395.97 | 80.447 | 0.2031 | 12.431 | 5.4755 | 8.2132
15 | 57.067 | 17.523 | 1.4495 | 1.6502 | 3256.7 | 3.1845 | 314.02 | 101.44 | 0.323 | 9.8579 | 4.3423 | 6.5134
16 | 50.82 | 19.677 | 1.2908 | 1.3086 | 2582.7 | 4.0156 | 249.03 | 127.91 | 0.5136 | 7.8177 | 3.4436 | 5.1654
17 | 45.257 | 22.096 | 1.1495 | 1.0378 | 2048.2 | 5.0636 | 197.49 | 161.3 | 0.8167 | 6.1997 | 2.7309 | 4.0963
18 | 40.302 | 24.813 | 1.0237 | 0.82307 | 1624.3 | 6.3851 | 156.62 | 203.39 | 1.2986 | 4.9166 | 2.1657 | 3.2485
19 | 35.89 | 27.863 | 0.9116 | 0.65268 | 1288.1 | 8.0514 | 124.2 | 256.47 | 2.0648 | 3.8991 | 1.7175 | 2.5762
20 | 31.961 | 31.288 | 0.8118 | 0.51759 | 1021.5 | 10.153 | 98.496 | 323.41 | 3.2832 | 3.0921 | 1.362 | 2.043
21 | 28.462 | 35.134 | 0.7229 | 0.41044 | 810.1 | 12.802 | 78.111 | 407.81 | 5.2205 | 2.4521 | 1.0801 | 1.6202
22 | 25.346 | 39.453 | 0.6438 | 0.32553 | 642.44 | 16.143 | 61.945 | 514.23 | 8.3009 | 1.9446 | 0.8566 | 1.2849
23 | 22.572 | 44.304 | 0.5733 | 0.25814 | 509.48 | 20.356 | 49.125 | 648.44 | 13.199 | 1.5422 | 0.6793 | 1.019
24 | 20.101 | 49.75 | 0.5106 | 0.20476 | 404.03 | 25.669 | 38.958 | 817.66 | 20.987 | 1.223 | 0.5387 | 0.8081
25 | 17.9 | 55.866 | 0.4547 | 0.16238 | 320.41 | 32.368 | 30.895 | 1031.1 | 33.371 | 0.9699 | 0.4272 | 0.6408
26 | 15.94 | 62.733 | 0.4049 | 0.12876 | 254.1 | 40.815 | 24.501 | 1300.1 | 53.061 | 0.7692 | 0.3388 | 0.5082
27 | 14.195 | 70.445 | 0.3606 | 0.10213 | 201.51 | 51.467 | 19.43 | 1639.4 | 84.371 | 0.61 | 0.2687 | 0.403
28 | 12.641 | 79.105 | 0.3211 | 0.080979 | 159.8 | 64.898 | 15.409 | 2067.3 | 134.15 | 0.4837 | 0.2131 | 0.3196
29 | 11.257 | 88.83 | 0.2859 | 0.064198 | 126.73 | 81.835 | 12.22 | 2606.8 | 213.31 | 0.3836 | 0.169 | 0.2535
30 | 10.025 | 99.75 | 0.2546 | 0.05091 | 100.5 | 103.19 | 9.6906 | 3287.1 | 339.18 | 0.3042 | 0.134 | 0.201
31 | 8.9276 | 112.01 | 0.2268 | 0.040399 | 79.702 | 130.12 | 7.685 | 4145 | 539.32 | 0.2413 | 0.1063 | 0.1594
32 | 7.9503 | 125.78 | 0.2019 | 0.032016 | 63.207 | 164.08 | 6.0945 | 5226.7 | 857.55 | 0.1913 | 0.0843 | 0.1264
33 | 7.0799 | 141.24 | 0.1798 | 0.02539 | 50.125 | 206.9 | 4.8332 | 6590.8 | 1363.6 | 0.1517 | 0.0668 | 0.1003
34 | 6.3048 | 158.61 | 0.1601 | 0.020131 | 39.751 | 260.9 | 3.8329 | 8310.8 | 2168.1 | 0.1203 | 0.053 | 0.0795
35 | 5.6146 | 178.11 | 0.1426 | 0.015971 | 31.524 | 328.99 | 3.0396 | 10480 | 3447.5 | 0.0954 | 0.042 | 0.063
36 | 5 | 200 | 0.127 | 0.012668 | 25 | 414.85 | 2.4105 | 13215 | 5481.7 | 0.0757 | 0.0333 | 0.05
37 | 4.4526 | 224.59 | 0.1131 | 0.010047 | 19.826 | 523.11 | 1.9116 | 16663 | 8716.2 | 0.06 | 0.0264 | 0.0397
38 | 3.9652 | 252.2 | 0.1007 | 0.0079643 | 15.723 | 659.63 | 1.516 | 21012 | 13859 | 0.0476 | 0.021 | 0.0314
39 | 3.5311 | 283.2 | 0.0897 | 0.0063194 | 12.469 | 831.78 | 1.2022 | 26496 | 22037 | 0.0377 | 0.0166 | 0.0249
40 | 3.1445 | 318.01 | 0.0799 | 0.005014 | 9.888 | 1048.9 | 0.9534 | 33410 | 35040 | 0.0299 | 0.0132 | 0.0198
AWG = American Wire Gauge size from 0000 to 40
Dia-mils = Diameter in mils (1 mil = .001 inch)
TPI = Turns Per Inch [Note that this is for BARE WIRE. Insulation thickness varies]
Dia-mm = Diameter in millimeters. This was included to help when dealing with metric Coilers.
Circ-mils = Cross sectional Area in Circular Mils. ( circular mils = diameter in mils squared )
Ohms/Kft = Ohms Per 1,000 ft.
Ft/Ohm = Number of feet required for 1 Ohm of resistance
Ft/Lb = Feet Per Pound
Ohms/Lb = Ohms Per Pound
Lb/Kft = Pounds Per 1,000 feet
*AMPS = Conservative Amp Rating based on 750 circulare mils per Amp
MaxAmps = Maximum allowable current based on 500 circular mils per Amp. Do NOT exceed this rating.